## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 38118664 | 38118664 | 0 | 0 | 125 | 125 | 0 | 0
11 | Land Cost | 74789 | 74789 | 0 | 0 | 0 | 0 | 0 | 0
12 | Site Permits | 28224 | 28224 | 0 | 0 | 0 | 0 | 0 | 0
13 | Plant Licensing | 28106000 | 28106000 | 0 | 0 | 92 | 92 | 0 | 0
14 | Plant Permits | 4490781 | 4490781 | 0 | 0 | 14 | 14 | 0 | 0
15 | Plant Studies | 5418869 | 5418869 | 0 | 0 | 17 | 17 | 0 | 0
20 | Capitalized Direct Costs | 88027947 | 31424998 | 0 | 0 | 289 | 103 | 0 | 0
21 | Structures and Improvements | 6883521 | 1834543 | 0 | 0 | 22 | 6 | 0 | 0
211 | Site Preparation/ Yard Work | 189155 | 108700 | 0 | 0 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 110808 | 63677 | 0 | 0 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 64481 | 37054 | 0 | 0 | 0 | 0 | 0 | 0
211.3 | Excavation | 13865 | 7967 | 0 | 0 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1218608 | 700286 | 0 | 0 | 4 | 2 | 0 | 0
212.1 | Reactor Building Slab Roof | 182165 | 104683 | 0 | 0 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 143288 | 82342 | 0 | 0 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 149614 | 85977 | 0 | 0 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 686143 | 394299 | 0 | 0 | 2 | 1 | 0 | 0
212.5 | Reactor Building HVAC | 57396 | 32983 | 0 | 0 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 71963 | 41354 | 0 | 0 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 47975 | 27569 | 0 | 0 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 14885 | 8554 | 0 | 0 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 11708 | 6728 | 0 | 0 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 21380 | 12286 | 0 | 0 | 0 | 0 | 0 | 0
213.2 | Control building | 23987 | 13784 | 0 | 0 | 0 | 0 | 0 | 0
213.21 | Control Building Slab Roof | 7442 | 4277 | 0 | 0 | 0 | 0 | 0 | 0
213.22 | Control Building Basement | 5854 | 3364 | 0 | 0 | 0 | 0 | 0 | 0
213.23 | Control Building Walls | 10690 | 6143 | 0 | 0 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 5365624 | 962268 | 0 | 0 | 17 | 3 | 0 | 0
214.7 | Emergency and Start-up Power Systems Building | 5330124 | 941867 | 0 | 0 | 17 | 3 | 0 | 0
214.72 | Diesel Generator | 5330124 | 941867 | 0 | 0 | 17 | 3 | 0 | 0
214.8 | Auxilliary Building | 35500 | 20400 | 0 | 0 | 0 | 0 | 0 | 0
214.81 | Maniplator Building | 35500 | 20400 | 0 | 0 | 0 | 0 | 0 | 0
214.811 | Manipulator Building Slab Roof | 5955 | 3422 | 0 | 0 | 0 | 0 | 0 | 0
214.812 | ManipulatorBuilding Basement | 17566 | 10094 | 0 | 0 | 0 | 0 | 0 | 0
214.813 | Manipulator Building Exterior Walls | 11978 | 6883 | 0 | 0 | 0 | 0 | 0 | 0
215 | Supply Chain Buildings | 38169 | 21934 | 0 | 0 | 0 | 0 | 0 | 0
215.1 | Storage Building | 38169 | 21934 | 0 | 0 | 0 | 0 | 0 | 0
215.11 | Storage Building Slab Roof | 14723 | 8461 | 0 | 0 | 0 | 0 | 0 | 0
215.12 | Storage Building Basement | 11581 | 6655 | 0 | 0 | 0 | 0 | 0 | 0
215.13 | Storage Building Walls | 11864 | 6818 | 0 | 0 | 0 | 0 | 0 | 0
22 | Reactor System | 48585560 | 10087943 | 0 | 0 | 159 | 33 | 0 | 0
221 | Reactor Components | 33738175 | 7464313 | 0 | 0 | 110 | 24 | 0 | 0
221.1 | Reactor Vessel and Accessories | 19796362 | 5109055 | 0 | 0 | 65 | 16 | 0 | 0
221.11 | Reactor Support | 3328787 | 859095 | 0 | 0 | 10 | 2 | 0 | 0
221.13 | Inner Vessel Structure - stainless_steel | 16467575 | 4249960 | 0 | 0 | 54 | 13 | 0 | 0
221.2 | Reactor Control Devices | 11320512 | 1892057 | 0 | 0 | 37 | 6 | 0 | 0
221.21 | Reactivity Control System | 11320512 | 1892057 | 0 | 0 | 37 | 6 | 0 | 0
221.211 | Reactivity Control System Fabrication | 4355582 | 694936 | 0 | 0 | 14 | 2 | 0 | 0
221.212 | Installation | 1016388 | 162165 | 0 | 0 | 3 | 0 | 0 | 0
221.213 | Control Drums Materials (Absorber) - B4C_natural | 4542330 | 802659 | 0 | 0 | 14 | 2 | 0 | 0
221.214 | Control Drums Materials (Reflector) - Graphite | 462491 | 81725 | 0 | 0 | 1 | 0 | 0 | 0
221.215 | Control System Drive Mechanism | 943719 | 150571 | 0 | 0 | 3 | 0 | 0 | 0
221.3 | Non-Fuel Core Internals | 2621299 | 463200 | 0 | 0 | 8 | 1 | 0 | 0
221.31 | Reflector | 1578476 | 278927 | 0 | 0 | 5 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | 956152 | 168958 | 0 | 0 | 3 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 622323 | 109968 | 0 | 0 | 2 | 0 | 0 | 0
221.32 | Shield | 203283 | 35921 | 0 | 0 | 0 | 0 | 0 | 0
221.322 | Out The Vessel Shield Materials - WEP | 203283 | 35921 | 0 | 0 | 0 | 0 | 0 | 0
221.33 | Moderator - monolith_graphite | 839540 | 148352 | 0 | 0 | 2 | 0 | 0 | 0
222 | Main Heat Transport System | 2087081 | 368800 | 0 | 0 | 6 | 1 | 0 | 0
222.2 | Reactor Heat Transfer Piping System - HPMR | 1740976 | 307641 | 0 | 0 | 5 | 1 | 0 | 0
222.3 | Heat Exchangers | 346105 | 61159 | 0 | 0 | 1 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 346105 | 61159 | 0 | 0 | 1 | 0 | 0 | 0
223 | Safety Systems | 3650182 | 645011 | 0 | 0 | 11 | 2 | 0 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 3650182 | 645011 | 0 | 0 | 11 | 2 | 0 | 0
223.21 | Rvacs (Cooling Vessel) | 1782498 | 314979 | 0 | 0 | 5 | 1 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 1867684 | 330031 | 0 | 0 | 6 | 1 | 0 | 0
227 | Reactor Instrumentation and Control (I&C) | 9077818 | 1604109 | 0 | 0 | 29 | 5 | 0 | 0
228 | Reactor Plant Miscellaneous Items | 32301 | 5707 | 0 | 0 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 7798252 | 4983930 | 0 | 0 | 25 | 16 | 0 | 0
232 | Energy Applications | 6746294 | 4798042 | 0 | 0 | 22 | 15 | 0 | 0
232.1 | Electricity Generation Systems | 6746294 | 4798042 | 0 | 0 | 22 | 15 | 0 | 0
236 | Common Instrumentation & Controls | 1051958 | 185887 | 0 | 0 | 3 | 0 | 0 | 0
24 | Electrical Equipment | 5151041 | 3663480 | 0 | 0 | 16 | 12 | 0 | 0
241 | Switchgear | 504013 | 358460 | 0 | 0 | 1 | 1 | 0 | 0
242 | Station Service Equipment | 419035 | 298022 | 0 | 0 | 1 | 0 | 0 | 0
243 | Switchboards | 136068 | 96773 | 0 | 0 | 0 | 0 | 0 | 0
244 | Protective Equipment | 390777 | 277925 | 0 | 0 | 1 | 0 | 0 | 0
245 | Electrical Structure & Wiring Container | 2107379 | 1498792 | 0 | 0 | 6 | 4 | 0 | 0
246 | Power & Control Wiring | 1593767 | 1133505 | 0 | 0 | 5 | 3 | 0 | 0
25 | Initial Fuel Inventory | 18310076 | 10625470 | 0 | 0 | 60 | 34 | 0 | 0
251 | First Core Mining | 4081264 | 4081264 | 0 | 0 | 13 | 13 | 0 | 0
252 | First Core Conversion | 334929 | 334929 | 0 | 0 | 1 | 1 | 0 | 0
253 | First Core Enrichment | 4559900 | 4559900 | 0 | 0 | 14 | 14 | 0 | 0
254 | First Core Fuel Assembly Fabrication - Yes | 9333980 | 1649375 | 0 | 0 | 30 | 5 | 0 | 0
26 | Miscellaneous Equipment (Cranes) | 1299496 | 229629 | 0 | 0 | 4 | 0 | 0 | 0
30 | Capitalized Indirect Services Cost | 9203738 | 3881354 | 0 | 0 | 30 | 12 | 0 | 0
31 | Factory & field indirect costs | 4137046 | 1105509 | 0 | 0 | 13 | 3 | 0 | 0
32 | Factory and construction supervision | 586129 | 201042 | 0 | 0 | 1 | 0 | 0 | 0
33 | Startup Costs | 2527524 | 1452469 | 0 | 0 | 8 | 4 | 0 | 0
34 | Shipping and Transportation Costs | 874273 | 502410 | 0 | 0 | 2 | 1 | 0 | 0
35 | Engineering Services | 645126 | 370728 | 0 | 0 | 2 | 1 | 0 | 0
36 | PM/CM Services | 433637 | 249194 | 0 | 0 | 1 | 0 | 0 | 0
40 | Capitalized training costs | 312000 | 312000 | 0 | 0 | 1 | 1 | 0 | 0
41 | staff recruitment and training | 312000 | 312000 | 0 | 0 | 1 | 1 | 0 | 0
60 | Capitalized Financial Costs | 2341510 | 1272689 | 0 | 0 | 7 | 4 | 0 | 0
62 | Interest | 2341510 | 1272689 | 0 | 0 | 7 | 4 | 0 | 0
70 | Annualized O&M Cost | 7468012 | 2896232 | 0 | 0 | 344 | 133 | 0 | 0
71 | O&M Staff | 1028445 | 1028445 | 0 | 0 | 47 | 47 | 0 | 0
711 | Operators | 7425 | 7425 | 0 | 0 | 0 | 0 | 0 | 0
712 | Remote Monitoring Technicians - Remotely Monitored | 92820 | 92820 | 0 | 0 | 4 | 4 | 0 | 0
713 | Security Staff | 928200 | 928200 | 0 | 0 | 42 | 42 | 0 | 0
73 | Regulatory Costs | 111467 | 111467 | 0 | 0 | 5 | 5 | 0 | 0
75 | Capital Plant Expenditures | 6268928 | 1723699 | 0 | 0 | 289 | 79 | 0 | 0
752 | Annualized Core Barrel Replacements | 2363713 | 610028 | 0 | 0 | 108 | 28 | 0 | 0
753 | Annualized Moderator Replacements | 381684 | 67446 | 0 | 0 | 17 | 3 | 0 | 0
754 | Annualized Reflector Replacements | 226570 | 40036 | 0 | 0 | 10 | 1 | 0 | 0
755 | Annualized Reactivity Control Replacements | 1624917 | 271581 | 0 | 0 | 74 | 12 | 0 | 0
759 | Annualized Misc. Replacements | 1672042 | 734607 | 0 | 0 | 77 | 33 | 0 | 0
78 | Annualized Decommissioning Cost | 59170 | 32620 | 0 | 0 | 2 | 1 | 0 | 0
80 | Annualized Fuel Cost | 8352795 | 4859108 | 0 | 0 | 385 | 224 | 0 | 0
81 | Refueling Operations | 5775 | 5775 | 0 | 0 | 0 | 0 | 0 | 0
82 | Additional Nuclear Fuel | 8324391 | 4830705 | 0 | 0 | 383 | 222 | 0 | 0
83 | Spent Fuel Management | 22627 | 22627 | 0 | 0 | 1 | 1 | 0 | 0
OCC | Overnight Capital Cost | 135662350 | 73737018 | 0 | 0 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 53834 | 29260 | 0 | 0 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 117352274 | 63111547 | 0 | 0 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 46568 | 25044 | 0 | 0 | - | - | - | -
TCI | Total Capital Investment | 138003861 | 75009707 | 0 | 0 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 54763 | 29765 | 0 | 0 | - | - | - | -
AC | Annualized Cost | 15820807 | 7755341 | 0 | 0 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 729 | 357 | 0 | 0 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 1182 | 603 | 0 | 0 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 383 | 194 | 0 | 0 | - | - | - | -

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | cross_sections_xml_location | /home/abderi/endfb-viii.0-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | Y |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /home/abderi/endfb-viii.0-hdf5/simplified_thermal_chain11.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 1000 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_natural |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | Helium |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Cooling Device | heatpipe |  | Primary heat removal device type (e.g. heatpipe for HPMR) | User Input
Materials | Enrichment | 0.19985 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | homog_TRISO |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | Moderator | monolith_graphite |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | TRISO Fueled | Yes |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | reactor type | HPMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 249.9565 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 31.991 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | Calculated
Geometry | Axial Reflector Thickness | 50 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Core Radius | 124.9783 | cm | Total core radius including the radial reflector | Calculated
Geometry | Fuel Assemblies Count | 18 |  | Total number of fuel assemblies in the core (HPMR) | Calculated
Geometry | Fuel Pin Count | 1296 |  | Total number of fuel pins (or fuel elements) in the entire core | Calculated
Geometry | Fuel Pin Count per Assembly | 72 |  | Number of fuel pins per hexagonal assembly (HPMR) | Calculated
Geometry | Fuel Pin Materials | ['homog_TRISO', 'Helium'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [1.0, 1.05] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Heat Pipe Materials | ['heatpipe', 'Helium'] |  | Ordered list of materials for each heat pipe region (HPMR) | User Input
Geometry | Heat Pipe Radii | [1.1, 1.15] | cm | Ordered list of radii defining heat pipe region boundaries (HPMR) | User Input
Geometry | Lattice Pitch | 3.4 | cm | Center-to-center distance between adjacent lattice positions | User Input
Geometry | Number of Heatpipes | 342 |  | Total number of heat pipes in the entire core (HPMR) | Calculated
Geometry | Number of Heatpipes per Assembly | 19 |  | Number of heat pipes per hexagonal assembly (HPMR) | Calculated
Geometry | Number of Rings per Assembly | 6 |  | Number of pin rings along the side of the hexagonal assembly (LTMR/HPMR) | User Input
Geometry | Number of Rings per Core | 3 |  | Number of assembly rings along the side of the hexagonal core (HPMR) | User Input
Geometry | Radial Reflector Thickness | 50 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
Geometry | hexagonal Core Edge Length | 86.5774 | cm | Edge length of the hexagonal core (HPMR) | Calculated
--- CONTROL DRUMS ---
Control Drums | All Drums Area | 15079.6447 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 3769255.7525 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 308.702 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 5834.8079 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 6143.51 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 12 |  | Total number of control drums in the core | Calculated
Control Drums | Drum Height | 249.9565 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 20 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 7851.2509 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Moderator Mass | 5295.8353 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Moderator Total Area | 12998.1748 | cm² | Total cross-sectional area occupied by moderator material in the core | Calculated
Core Design | Radial Reflector Mass | 12062.8558 | kg | Total mass of the radial neutron reflector | Calculated
--- OVERALL SYSTEM ---
Overall System | Heat Flux | 0.032754 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 2.52 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 7 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.36 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
Overall System | Time Steps | [864.0, 85536.0, 259200, 518400, 1728000, 6048000, 8640000, 14256000, 31536000, 31536000, 31536000, 31536000, 31536000, 31536000, 31536000.0] | s | User-specified depletion step durations used by the integrator | User Input
--- OPENMC SETTINGS ---
OpenMC Settings | Cold Shutdown Temperature | 300 | K | Temperature used for the shutdown-state (ARI) keff calculation during shutdown margin evaluation. | User Input
OpenMC Settings | Isothermal Temperature Coefficients | FALSE |  | Whether isothermal temperature reactivity coefficients were calculated | User Input
OpenMC Settings | Shutdown Margin Calc | FALSE |  | Whether shutdown margin is calculated. When True, the shutdown-state keff is evaluated with the absorber facing the core (ARI) at Cold Shutdown Temperature, and shutdown margin metrics are reported from ((1 - k_s) / k_s). | User Input
--- PHYSICS RESULTS ---
Physics Results | BOL Axial Non-Leakage Probability | 0.97763 | fraction | Beginning-of-life axial non-leakage probability from the 2D-to-3D buckling correction model. | Calculated
Physics Results | BOL Total Non-Leakage Probability | 0.88816 | fraction | Beginning-of-life total non-leakage probability from the axial-plus-radial buckling model. Returns NaN when Core Radius is not available. | Calculated
Physics Results | Depletion Time Steps | [0.0, 0.01, 1.0, 4.0, 10.0, 30.0, 100.0, 200.0, 365.0, 730.0, 1095.0, 1460.0, 1825.0, 2190.0, 2555.0, 2920.0] | days | Calculated cumulative depletion times corresponding to the reported keff values and used as the x-axis in keff_comparison_vs_Time.png. | Calculated
Physics Results | Estimated Axial Leakage (%) | 2.2375 | % | Estimated beginning-of-life axial neutron leakage percentage from the axial buckling correction model, computed as 100 × (1 - axial non-leakage probability). | Calculated
Physics Results | Estimated Total Leakage (%) | 11.1838 | % | Estimated beginning-of-life total neutron leakage percentage from the axial-plus-radial buckling model, computed as 100 × (1 - total non-leakage probability). Returns NaN when Core Radius is not available. | Calculated
Physics Results | Fuel Lifetime | 893 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Tail Waste Mass | 21864.8749 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Mass U235 | 103226.6186 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 418581.0308 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Maximum Shutdown Margin 2D | N/A | pcm | Maximum shutdown margin from the 2D simulation, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Maximum Shutdown Margin 3D (2D corrected) | N/A | pcm | Maximum shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 2D | N/A | pcm | Most limiting shutdown margin from the 2D simulation, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) | N/A | pcm | Most limiting shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Natural Uranium Mass | 22386.6825 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | SWU | 21726.0485 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Temp Coeff 2D | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient from the 2D simulation. Negative values indicate self-stabilizing behavior. Note: 2D simulation overestimates keff — use 3D corrected value for safety conclusions. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient corrected from 2D to 3D using axial neutron leakage correction. Negative values confirm self-stabilizing behavior. Use this value for safety analysis. | Calculated
Physics Results | Uranium Mass | 521.8076 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
Physics Results | keff 2D | [1.0777848133353216, 1.0708276572432132, 1.0745072296509481, 1.0712037094818134, 1.0670685728447895, 1.0709828415072566, 1.0619224564474166, 1.0632622758402146, 1.0476923160778933, 1.0296691410360101, 1.013877130166069, 1.0036667123725604, 0.9859558928057377, 0.9725402219393405, 0.9668807751167359, 0.9391740049121774] |  | keff at each burnup step for the operating configuration (ARO) from the 2D OpenMC simulation, evaluated at Common Temperature. | Calculated
Physics Results | keff 3D (2D corrected) | [1.0536696321465522, 1.0470801235093488, 1.050814546577607, 1.0476357780279864, 1.0434273134702832, 1.0471876708080137, 1.0385374556399705, 1.0398466070366685, 1.0244608092754297, 1.0068729624946515, 0.9915078117348135, 0.9819652784454141, 0.9647058741332979, 0.9516196975322135, 0.9460421382849689, 0.9189348677493928] |  | keff at each burnup step for the operating configuration (ARO), corrected from 2D to 3D using axial leakage correction and evaluated at Common Temperature. | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 1260 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Primary HX Mass | 1450.6623 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Count | 2 |  | Number of primary coolant loops | User Input
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 923.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 923.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Loop Purification | TRUE |  | Whether primary coolant purification is used (reduces coolant replacement frequency) | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 573.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 903.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 124.9783 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 0 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 124.9783 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 0 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 9868.1099 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 39.37 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Outer Radius | 176.8483 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 1643.9697 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 131.9783 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 5 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 0 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 0 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | low_alloy_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 126.9783 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 0 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 1722.5348 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 136.9783 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Total Vessels Mass | 9547.3708 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 417.1085 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 20 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 6180.8664 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 124.9783 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 2 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 461.7375 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 137.4783 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Core Barrel Replacement Period (cycles) | 4 | cycles | Number of fuel cycles between scheduled core barrel replacements | User Input
Operation | A75: Drum Replacement Period (cycles) | 4 | cycles | Number of fuel cycles between scheduled control drum replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 4 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A75: Vessel Replacement Period (cycles) | 4 | cycles | Number of fuel cycles between scheduled reactor pressure vessel replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Electricity Production | 21688.128 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.98247 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 60 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of Operators | 2 |  | Number of operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 0 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | Remotely Monitored |  | Reactor operation mode: Remotely Monitored or On-Site Staffed | User Input
Operation | Reactors Monitored Per Operator | 10 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 7 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 0 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 1 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Debt To Equity Ratio | 1 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 0.02 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.015556 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 1 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- LEARNING RATES ---
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
--- DEBUG / INTERMEDIATE VALUES ---
Debug / Intermediate Values | keff 2D ARO (BOL) | 1.0778 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 2D ARO (EOL) | 0.93917 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 2D ARO (min) | 0.93917 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 2D ARO (max) | 1.0778 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (BOL) | 1.0537 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (EOL) | 0.91893 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (min) | 0.91893 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (max) | 1.0537 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — maximum value | Calculated
--- UNCATEGORIZED ---
Uncategorized | Outer Shield Inner Radius | 137.4783 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown